## Slide 1
AVR Course
Modbus RTU
Hossein Zivarian

## Slide 2
Requirements

## Slide 3
Modbus is an industrial protocol that was developed in 1979 to make communication possible between automation devices.
Modbus is a request-response protocol implemented using a master-slave relationship. In a master-slave relationship, communication always occurs in pairs—one device must initiate a request and then wait for a response—and the initiating device (the master) is responsible for initiating every interaction.

## Slide 4
Modbus OSI Model

## Slide 5
Modbus RTU Message Format

## Slide 6
Modbus Function Codes

## Slide 7
Function Code 01 (Read Coils)
Slave Address
Function Code
Starting Address Hi
Starting Address Lo
No. of Points Hi
No. of Points Lo
CRC Hi
CRC Lo
Query
Slave Address
Function Code
Byte Count
Data
CRC Hi
CRC Lo
Response
11
01
00
13
00
25
0E
84
11
01
05
CD 6B B2 0E 1B
45
E6

## Slide 8
Function Code 02 (Read Discrete Inputs)
Slave Address
Function Code
Starting Address Hi
Starting Address Lo
No. of Points Hi
No. of Points Lo
CRC Hi
CRC Lo
Query
Slave Address
Function Code
Byte Count
Data
CRC Hi
CRC Lo
Response
11
02
00
C4
00
16
BA
A9
11
02
03
AC DB 35
20
18

## Slide 9
Function Code 03 (Read Holding Registers)
Slave Address
Function Code
Starting Address Hi
Starting Address Lo
No. of Points Hi
No. of Points Lo
CRC Hi
CRC Lo
Query
Slave Address
Function Code
Byte Count
Data
CRC Hi
CRC Lo
Response
11
03
00
6B
00
03
76
87
11
03
06
AE41 5652 4340
49
AD

## Slide 10
Function Code 04 (Read Input Registers)
Slave Address
Function Code
Starting Address Hi
Starting Address Lo
No. of Points Hi
No. of Points Lo
CRC Hi
CRC Lo
Query
Slave Address
Function Code
Byte Count
Data
CRC Hi
CRC Lo
Response
11
04
00
08
00
01
B2
98
11
04
02
000A
F8
F4

## Slide 11
Function Code 05 (Write Single Coil)
Slave Address
Function Code
Starting Address Hi
Starting Address Lo
Write Status Hi
Write Status Lo
CRC Hi
CRC Lo
Query
Response
11
05
00
AC
FF
00
4E
8B
Slave Address
Function Code
Starting Address Hi
Starting Address Lo
Write Status Hi
Write Status Lo
CRC Hi
CRC Lo
11
05
00
AC
FF
00
4E
8B

## Slide 12
Function Code 15 (Write Multiple Coils)
Slave Address
Function Code
Starting Address Hi
Starting Address Lo
No. of Coils Hi
No. of Coils Lo
CRC Hi
CRC Lo
Query
Response
11
0F
00
13
00
0A
BF
0B
Slave Address
Function Code
Starting Address Hi
Starting Address Lo
No. of Coils Hi
No. of Coils Lo
CRC Hi
CRC Lo
11
0F
00
13
00
0A
26
99
Byte Count
02
Write Value
CD01

## Slide 13
Temperature & Humidity Sensor Module
XY-MD02

## Slide 14
Temperature & Humidity Sensor Module
XY-MD02

## Slide 15
Temperature & Humidity Sensor Module
XY-MD02